SPECIFICATION

FOR APPROVAL

Part name：Din-Rail Terminal Block(RTB)H

Part   No.：RTB404-08-01-2

Cust.  P/N：

Date：2008-2-19

Seller Confirmation              Customer Confirmation

| Written by | Qiang.Zhou |  | Project Audit |  |
| --- | --- | --- | --- | --- |
| Checked by | Shangyang.Yi |  | Structure Audit |  |
| Approved by | Jim |  | Security Certification |  |
|  |  |  | Quality Approval |  |

Supplier :  Hangzhou antron electronics Co., Ltd.

Address :  No.639 , Deng yun Road , Hangzhou China

Tel :                         0571-89902210

Fax :       0571-89908128

Postcode:  310011

E-mail :   anqiao@263.net

Customer: Customer P/N: Seller: Hangzhou antron electronics Co., Ltd. Part No: RTB404-08-01-2

Revision for RTB404-08-01-2

| Item No | Edition | Part Revised | Date Revised |
| --- | --- | --- | --- |
| 1 | A | put in file | 2008-2-19 |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |
| 9 |  |  |  |

1.TYPE：RTB404-08-01-2

2.DRAWING&SIZES

OVERALL SIZES

| TOLERANCE： ＞120 | ±0.80 |
| --- | --- |
| ＞30～120 | ±0.50 |
| ＞6～30 | ±0.40 |
| 0～6 | ±0.25 |

3.BOM TABLE

| ITEM. | PART NAME | MATERIAL | SURFACE OF CONTACT | QUANTITY(PCS) |
| --- | --- | --- | --- | --- |
| (1) | L-SCREW | BRASS | Nickel Plated 5um | 2 |
| (2) | S-SCREW | BRASS | Nickel Plated 5um | 2 |
| (3) | BLOCK | BRASS | Nickel Plated 5um | 4 |
| (4) | BODY | PA66 |  | 1 |
| (5) | CONTACT | COPPER | Nickel Plated 5um | 1 |

4.TECHNICAL DATA:

WIRE RANGE：             12～24AWG

MAX. TORQUE：            4.4 L	bf.in

ELECTRICAL RATING：     600V, 30A.

DIELECTRIC WITHSTAND：  AC3000V, 1 minute

BREAKDOWN VOLTAGE:     8000V (1.2/50μs),

CROSS SECTION：          4mm2

STRIPPING LENGTH：       8mm

5.WORKING CONDITION：

OPERATING TEMPERATURE：-40℃～+105℃

ALTITUDE：                  Less than 2000m 40Kpa～80KPa

RELATIVE HUMIDITY：       5%～95%

POLLUTION DEGREE：       Ⅲ

6.APPLICABLE STANDARDS

IEC 60947-1:2001    IEC 60947-7-1:2002    UL 1059:2001

7.ACCESSORIES

MOUNTING RAIL:      JNS35:7.5/JNS35:15/JNS32

COVER:               A070-0

SEPARATING PLATE： A060-0

MARKING STRIP:      A061-10-5

STATOR：             A047-0

8.PROCEDURE

Wires can be connected with this type of terminal blocks by a manua or automatic screwdriver.

9. PACKAGE

Tightly Sealed